Diocese of Middlesbrough

Inspections – Compliance Guidance

| Types of System/Plant | Action required | Frequency | Inspection by | Type of Inspection | Relevant legislation and/or Guidance |
| --- | --- | --- | --- | --- | --- |
| Fire and Smoke |  |  |  |  | BS9999:2008 Code of Practice for fire safety in the design, management and use of buildings |
| Fire Extinguishers | Inspection Discharge (Not CO2) | 12 Monthly 60 monthly | Competent Person (Accredited Company) | Statutory Statutory | BS EN 3:2000 Portable Fire Extinguishers BAFE, LPC or similar |
| Fire detection & Alarm systems | Functional check Inspection Inspect and Test | Weekly 3 monthly 12 monthly | User Competent person (Accredited company) | Operational Operational Statutory | BS 5839-1:2013 Fire detection and alarm systems Code of Practice Loss prevention Standard 1014 requirements for Fire detection and alarm systems installers. FIA, LPC or similar |
| Fire hose reels | Visual Inspection Function Test | 1 monthly 12 monthly | User Trained person | Risk Assessment Risk Assessment | BS EN 694:2001 Fire hose reels BS EN 671-3:2009 Fixed fire lighting systems |
| Non Automatic Fire Protection system Dry (or Wet) Risers and hydrants | Visual inspection Inspection Hydraulic test | Weekly 6 monthly 12 monthly | User Competent person (Accredited company) | Statutory | BS EN 671 BS 9990:2006 and BS 5306-1:2006. BS588-12 and Building Regulations FIA, LPC or similar accreditation |
| Automatic sprinkler protection systems Wet system (Wet/Dry) Dry system Pre-engaged Fire pumps | Depends on type and purpose– Risk based | Weekly 1 monthly 3 monthly 6 monthly 12 monthly | Trained person Competent person (Accredited company) | Operational Operational Operational Statutory Statutory | BS 12845 2004 Automatic sprinkler systems LPCB certificate of conformity BS 9251 Sprinkler systems for residential and domestic occupancies (CoP) FIA, LPC or similar |
| Escape routes Fire doors | Visual inspection Auto doors Inspection | Weekly 1 Monthly 6 monthly | User User Competent person | Operational Operational | HSWA Section 2 Building Regulations BS999:2008 |
| Fire System Risk Assessment | Risk Assessment | As specified in RA or through change | Competent person (Accredited company) | Statutory | Risk Assessment specifies the criteria for the management of fire systems |
| Health and Safety |  |  |  |  |  |
| Asbestos | Risk Assessment Inspection Training | Kept up to date and managed. As per Risk Assessment Annual training for those potentially exposed | User User Competent person | Statutory Statutory Operational | Control of Asbestos Regulations 2006 Control of Asbestos Regulations 2006 Control of Asbestos Regulations 2006 |
| Noise | Risk assessment | Assessment report | Competent person | Statutory | Control of Noise at Work Regulations 2005 |
| Substances Hazardous to Health (COSHH) | Data sheets, method statements, records, COSHH register | As required | Competent person | Statutory | Control of Substances Hazardous to Health Regulations 2002 (COSHH) |

| Types of System/Plant | Action required | Frequency | Inspection by | Type of Inspection | Relevant legislation and/or Guidance |
| --- | --- | --- | --- | --- | --- |
| Health & Safety contd… |  |  |  |  |  |
| Water systems |  |  |  |  |  |
| Water Hygiene Assessment Management Control of Legionellosis | Risk Assessment Cold water storage and tap temperatures Laboratory Samples | As per Risk Assessment As per Risk Assessment As per Risk Assessment | Competent person User/competent person Accredited company Competent Person | Statutory Operational Operational | HSE ACoP L8 Prevention & Control of Legionellosis BS 8580 risk assessment for the control of Legionella in water systems Control of Substances Hazardous to Health Regulations 1999 (COSHH) |
| Hazard Risk Assessment | Identification of: Trip, slip, head injuries, working at height, confined spaces, hazardous areas, emergency preparation Fire Risk Assessment | At least annually Subject to Risk Assessment | Responsible Person Competent Person | Statutory Statutory | MHSWR 1999 (Management of Health and Safety at Work Regulations 1999) Fire Reform (Fire Safety) Order 2005 |
| Energy & Environment |  |  |  |  |  |
| Water for domestic use within buildings Effluent discharge (septic tanks straight to water course) | Use of correct fittings Notice permitting discharges Emptying | Flushing & cleaning certificate; chlorination certificate Minimum annually | Competent Persons Environmental Agency Competent Person | Operational Operational Operational | BS 6700 2006 & Al 2009 Design etc water for domestic use within buildings Water regulations 1999 Water Industry Act 1991 (Section 119) |
| Drainage Interceptors | Physical Inspection Emptied and internal inspection | 6 months 5 years | Competent Person Competent Person | Operational Operational | BS EN858-2 (2003) PPG3 |
| Oil Storage Installation Above Ground >200L<3500L>3500L | Bund (water/leaks) Installation – Condition and limits tests report Pipework Underground | Weekly Annually 5 or 10 years | User Competent Person Competent Person | Operational Operational Pressure Test | Control of Pollution (Oil Storage) (England) Regulations 2001 or the Water Environment (Oil Storage) (Scotland) Regulations 2006. Section J of the Building Regulations. Pollution Prevention Guidance 2 OFTEC ~Technical Book 1 and 3 |

| Types of System/Plant | Action required | Frequency | Inspection by | Type of Inspection | Relevant Legislation and/or Guidance |
| --- | --- | --- | --- | --- | --- |
| Energy & Environment contd… |  |  |  |  |  |
| Waste Disposal | Display ‘Transfer of Waste’ certificate | Each disposal |  | Statutory | Environmental Protection Act 1990 |
| WEEE | Dispose of equipment via a registered collector | Each disposal |  | Statutory | Waste Electrical & Electronic Equipment Regulations 2007 Environmental Protection (Duty of Care) Regulations 1991 The Hazardous Waste (England and Wales) Regulations 2005 |
| Display energy certificates (public buildings over 1000m2) | Building inspection and certification | 12 monthly | Competent Person | Statutory | Energy Performance of Buildings (certificates and inspections) Regulations 2007 |
| Energy Performance Certificate | Building inspection and certification | On construction, sale or rent (Listed Buildings currently exempt) | Competent Person | Statutory | Energy Performance of Buildings (certificates and inspections) Regulations 2007 |
| Air-conditioning inspections | A/C system inspection and certification greater than 12kw cooling load | Inspection 60 monthly | Accredited Person | Statutory | Energy Performance of Buildings (certificates and inspections) Regulations 2007 CIBSE TM44 |
| Boiler Inspections |  |  |  |  | EU Energy performance of Buildings Directive |
| Oil | Combustion check and boiler service (Landlord Certificate) | 6 monthly | OFTEC certified company Competent Person | Operational | ISO 14001:2004 Environmental Management Systems |
| Gas | Combustion check and boiler service (Landlord Certificate) | 12 months | Gas Safe certified company Competent Person | Statutory | Gas Safety (installation and use) Regulations 1998 |
| Electrical (including lighting) |  |  |  |  |  |
| Electrical installations and equipment |  |  |  |  |  |
| Includes fixed electrical, control panels Electrical Installation Condition Report | Visual and functional checks Thorough Inspection and test | 60 monthly Subject to previous report or 5 years, whichever is sooner | Competent Person Competent Person | Operational Statutory | Inspection is required by our insurers BS7671:2008 IET Wiring Regulations |
| Portable Electrical Appliances (PAT) |  |  |  |  |  |
| A portable appliance in a low risk area is an electrical appliance that can be plugged in, or moved whilst connected to an electrical supply, and includes some fixed appliances Offices Halls Churches Presbyteries | Pre-use checks | At suitable intervals 12 months 12 months 12 months 24 months | User Competent person (C+G2377) | Operational | The Health & Safety at Work Act 1974 (HSW) The Management of the Health & Safety at Work Act regulations 1999 (MHSWR) The Provision and Use of Work Equipment Regulations 1999 (PUWER) The Electricity at Work Regulations 1989 (EAWR) HSE HSG107 Maintaining portable and transportable electrical equipment HSE INDG236 Maintaining portable equipment in offices |

| Types of System/Plant | Action required | Frequency | Inspection by | Type of Inspection | Relevant Legislation and/or Guidance |
| --- | --- | --- | --- | --- | --- |
| Electrical contd… |  |  |  |  |  |
| Emergency Lighting |  |  |  |  |  |
| The continued operation of emergency lighting is imperative and testing is required to ensure it remains in a serviceable condition. Logbook record required | Full discharge for self-contained fitting 36 months after installation and then annually Indicators of central power supplies (green lights) Short Duration Test 3 hour discharge test | Daily Monthly 12 monthly | Competent Person User User Competent person | Statutory Operational Operational Statutory | The Electricity at Work Regulations 1989 (EAWR) The Health & Safety at Work Act 1974 (HSW) BSEN 50172:2004 (BS5266-8:2004) Emergency Escape Lighting Systems The frequency of inspection and testing may change subject to assessment or building type |
| Lightning Conductors |  |  |  |  |  |
| Lightning protection and earthing systems | Condition and inspection report | 11 monthly (indicative) | Competent Person | Operational | The Electricity at Work Regulations 1989 (EAWR) The Health & Safety at Work Act 1974 (HSW) BSEN 62305 (1-4) 2006 Protection against Lightning |
| Local Authority Entertainments Licencing |  |  |  |  |  |
| As required by Local Authority for public areas, includes emergency lighting and Lightning protection | Local Authority mandates | 12 monthly or as required | Competent Person | Statutory | The Management of the Health & Safety at Work Act regulations 1999 (MHSWR) The Electricity at Work Regulations 1989 (EAWR) |
| Lifts, Escalators, Lifting Equipment |  |  |  |  |  |
| Passenger Lifts |  |  |  |  |  |
| All lifting equipment used to lift or lower persons | Service Engineering inspections | Risk Assessment 6 monthly | Accredited Company Competent person Accredited Company Competent person | Operational Statutory | Lifting Operations and Lifting Equipment Regulations 1998 (LOLER) Provision and use of Work Equipment Regulations 1998 (PUWER) The Electricity at Work Regulations 1989 (EAWR) The Management of the Health & Safety at Work Act regulations 1999 (MHSWR |

| Types of System/Plant | Action required | Frequency | Inspection by | Type of Inspection | Relevant Legislation and/or Guidance |
| --- | --- | --- | --- | --- | --- |
| Lifts, Escalators, Lifting Equipment contd… |  |  |  |  |  |
| Lifts & Hoists |  |  |  |  |  |
| Lift used for lifting goods and equipment only | Service Engineering Inspections | Risk Assessment 12 monthly | Accredited Company Competent Person Accredited Company Competent Person | Operational Statutory | Lifting Operations and Lifting Equipment Regulations 1998 (LOLER) Provision and use of Work Equipment Regulations 1998 (PUWER) The Electricity at Work Regulations 1989 (EAWR) The Management of the Health & Safety at Work Act regulations 1999 (MHSWR |
| Escalators |  |  |  |  |  |
| Includes stair lift conveyor, horizontal and vertical conveyor walks | Service | 6 monthly | Competent Person | Statutory | Lifting Operations and Lifting Equipment Regulations 1998 (LOLER) Provision and use of Work Equipment Regulations 1998 (PUWER) The Electricity at Work Regulations 1989 (EAWR) |
| Mechanical Plant |  |  |  |  |  |
| Hot Water Boilers (>100oC) Heating systems MTHW and HTHW (Medium temperature hot water and high temperature hot water system) | Provision of written scheme of examination | 14 monthly | Competent Person Independent and minimum Incorporated Engineer | Statutory | Pressure Systems Safety Regulations 2000 (PSSR) Provision and Use of Work Equipment Regulations 1998 (PUWER) The Electricity at Work Regulations 1989 (EAWR) HSC ACOP L122 Safety of Pressure Systems |
| Steam Boiler and Steam Ovens generating high pressure hot water or steam | Provision of written scheme of examination | 14 monthly | Competent Person Independent Chartered Engineer | Statutory | Pressure Systems Safety Regulations 2000 (PSSR) Provision and Use of Work Equipment Regulations 1998 (PUWER) The Electricity at Work Regulations 1989 (EAWR) HSC ACOP L122 Safety of Pressure Systems |
| Other Pressure Vessels – All other non-steam vessels containing a relevant fluid, used to hold gases or liquids at high pressure >250 BarLitres | Provision of written scheme of examination | 26 monthly | Competent Person | Statutory | Pressure Systems Safety Regulations 2000 (PSSR) Provision and Use of Work Equipment Regulations 1998 (PUWER) The Electricity at Work Regulations 1989 (EAWR) |
| Gas installation – Landlord annual safety check for tenanted premises | Safety Certificate | 12 monthly | Competent Person Gas Safe Registration | Statutory | Gas Safety (Installation and Use) Regulations 1998 (SI 1998 No 2451) HSC ACOP L56 Safety in the installation and use of gas systems and appliances |

| Types of System/Plant | Action required | Frequency | Inspection by | Type of Inspection | Relevant Legislation and/or Guidance |
| --- | --- | --- | --- | --- | --- |
| Mechanical Plant contd… |  |  |  |  |  |
| Ventilation System | Risk Assessment | Risk Assessment | Competent Person to TR/19 Standard | Operational | MHSWR 1992 (Reg 5 and 6) HVCA TR/19 |
| Kitchen Extract | Part of Fire Risk Assessment | Risk Assessment | Competent Person to TR/19 Standard | Statutory | Fire Regulations HVCA DW/172 |
| Powered Mechanical Closers | Where a person may become trapped in a closing door | 12 monthly | Competent Person | Statutory | BS7036 |
| Premises Inspections |  |  |  |  |  |
| Churches and Halls | Visual Inspection (written results) Visual Inspection | Monthly 5 yearly | User Competent person | Operational Operational | Required by insurers Required by insurers, and HCC in the case of listed buildings |